WEEK 3

ADVANCED STUDY DOCUMENT

GET Estimation & Costing Engineer

Complex Estimation  |  Risk & Commercial Management  |  Project Execution

| Role GET – Estimation & Costing Engineer | Week Week 3 – Advanced | Topics Complex Estimation, Risk & Commercial |
| --- | --- | --- |

# 1. Week 3 Overview & Advanced Objectives

Week 3 is the advanced training phase. You will move beyond component-level estimation into complex multi-panel system estimation, project risk analysis, commercial negotiation fundamentals, and lifecycle cost analysis. This week also covers specialist panel types, large-scale industrial projects, and the skills required to lead an estimation team.

## 1.1 Advanced Learning Objectives

- Develop complex multi-panel system estimates for large industrial projects

- Perform and document risk assessments for estimation and project delivery

- Understand lifecycle costing and total cost of ownership (TCO) analysis

- Apply value engineering techniques to improve panel cost competitiveness

- Understand contract types, commercial terms, and negotiation basics

- Develop and manage estimation schedules, resources, and review processes

- Handle specialist panel types: ATEX/IECEx, SIL-rated, marine, modular substations

- Understand international projects, export, and currency risk management

## 1.2 Week 3 Study Plan

| Day | Topic | Key Focus | Duration |
| --- | --- | --- | --- |
| Day 1 | Complex System Estimation | Multi-panel, interconnections, I/O lists, cable schedules | 8 hrs |
| Day 2 | Risk & Lifecycle Cost Analysis | Risk register, contingency, TCO, LCC analysis | 8 hrs |
| Day 3 | Specialist Panel Types | ATEX, SIL, marine, modular substation, e-house | 8 hrs |
| Day 4 | Commercial & Contract Management | Contract types, claims, variations, negotiation | 8 hrs |
| Day 5 | Capstone Project | Full multi-panel estimate for a real-world scenario | 8 hrs |

# 2. Complex Multi-Panel System Estimation

Large industrial projects (mining, oil & gas, water treatment, power generation) typically require multiple panels that are interconnected. The estimator must understand not only the individual panel costs but also the system-level requirements: inter-panel cabling, communications infrastructure, earthing systems, and integration testing.

## 2.1 Typical Multi-Panel System Configurations

| System Type | Typical Panel Mix | Industry | System Complexity |
| --- | --- | --- | --- |
| Pump station automation | MCC + PLC panel + SCADA workstation | Water / wastewater | Medium |
| Mine conveyor control | Multiple MCCs + VFD panels + PLC + network | Mining | High |
| Process plant (batch) | MCC + PLC + SCADA + HMI stations + field junction boxes | Chemical/pharma | Very High |
| Offshore platform | MCC (ATEX) + SIL PLC + VFD + ESD panel + F&G panel | Oil & gas | Extreme |
| Water treatment plant | Multiple MCCs + PLC + SCADA + telemetry RTU | Water authority | Medium-High |
| Building services BMS | LV board + VFDs + BMS DDC panels + network | Commercial building | Medium |
| Power station auxiliary | HV/LV MCCs + excitation + protection relays + DCS I/O | Power generation | Extreme |

## 2.2 System-Level Estimation Items

Beyond individual panel costs, the following system-level items must be included in a multi-panel estimate:

### Inter-Panel Cabling

- Power cables between panels (MCC to VFD bypass, MCC to distribution boards)

- Control cables (PLC panel to MCC for remote start/stop, status feedback)

- Communication network cables (Profibus, Profinet, Modbus, Ethernet – fibre or copper)

- Allow for cable trays, conduit, and supporting infrastructure within skid or e-house

### Earthing & Bonding System

- Earth bar system for each panel (common earth bus in e-house or substation)

- Equipotential bonding between all enclosures

- Instrument earth (isolated from power earth for sensitive analogue circuits)

- Lightning protection earth (if outdoor installation)

### Auxiliary Systems

- UPS system (centrally rated for full control system load)

- Communication infrastructure (fibre patch panels, managed network switches, patch leads)

- Air conditioning for control room or e-house (centralised)

- Panel lighting (if in e-house or building)

- CCTV / access control (if part of scope)

### Integration & System Testing

- System integration test (SIT): Testing all panels together as a system before shipment

- Inter-panel communication test: Verify all data exchange across fieldbus and network

- Power-on sequence test for full system

- Emergency shutdown (ESD) system test – if applicable

Advanced Estimation Principle

On large projects, system-level costs (inter-panel cabling, earthing, communications, integration testing) can represent 15–25% of total panel scope cost. New estimators commonly focus only on individual panels and miss these items entirely, resulting in significant underestimation. Always develop a system-level checklist in addition to individual panel BOMs.

## 2.3 Cable Schedule Development for Estimation

A cable schedule lists every cable in the system. For estimation, a summary cable schedule is used to price inter-panel and field cabling:

| Cable Schedule Field | Description | Purpose in Estimation |
| --- | --- | --- |
| Cable Tag | Unique reference (e.g., C-001, P-MCC-001) | Tracking and ordering |
| From / To | Origin and destination of cable | Routing and length calculation |
| Cable Type | PVC/PVC, XLPE, Screened, LSZH, FP | Determines unit rate |
| Cable Size (mm²) | Cross-sectional area of conductors | Current capacity check + unit rate |
| Number of Cores | 3-core, 4-core, 7-core, 12-pair, etc. | Determines cable price |
| Estimated Length (m) | Route length + 10–15% waste allowance | Total cable quantity |
| Gland Qty | 2 glands per cable (both ends) | Additional material cost |
| Lug / Ferrule Qty | Per core at each end | Labour and material cost |
| Special Requirements | Armoured, fire rated, ATEX, double screened | Premium pricing trigger |

## 2.4 Estimation for E-House / Modular Substation

An E-House (Electrical House) is a prefabricated, self-contained building that houses electrical switchgear, MCCs, VFDs, PLCs, and associated equipment. Increasingly popular in mining and oil & gas projects.

- Structural: Containerised (20ft/40ft ISO container) or purpose-built steel building

- Electrical: Internal cable trays, earth grid, lighting, power outlets, UPS

- HVAC: Air conditioning sized for full electrical heat load + occupancy

- Fire protection: Gas suppression or FM200 system, smoke detectors

- Access: Personnel door, equipment access door (for future maintenance removal)

- Lifting: Lifting lugs, crane spreader bar (for shipping and installation)

- Skid design: Loadout design for sea freight (ISO container dimensions are critical)

| E-House Cost Element | Typical % of E-House Cost | Notes |
| --- | --- | --- |
| Structural / building shell | 15–25% | Steel fabrication, insulation, cladding |
| Electrical panels & equipment inside | 40–60% | MCC, VFD, PLC, switchgear |
| Internal cabling & earthing | 8–15% | Intra-E-house wiring |
| HVAC system | 5–10% | Air conditioning, ventilation |
| Fire & gas detection system | 3–6% | Detectors, alarm, suppression |
| Lighting & small power | 2–4% | LED lighting, GPOs, emergency lighting |
| Engineering & design | 8–15% | Structural calcs, electrical design, documentation |
| Transportation & installation | 5–10% | Crane, transport, site connection |

# 3. Risk Analysis & Contingency in Estimation

Every estimate carries risk. Advanced estimators identify, quantify, and price risk explicitly rather than hiding it in inflated unit rates. A structured risk approach makes estimates more transparent, defensible, and competitive.

## 3.1 Types of Estimation Risk

| Risk Category | Examples | Typical Impact |
| --- | --- | --- |
| Scope uncertainty | Incomplete drawings, preliminary I/O list, no spec issued | +10–30% contingency |
| Technical complexity | First-of-kind technology, complex safety system | +5–20% |
| Supply chain risk | Long lead items, single-source components, global shortage | +5–15% |
| Labour productivity | New workforce, specialist skills shortage, shift work | +10–25% |
| Client-driven changes | Specification changes during manufacture (variations) | +5–15% |
| Testing requirements | Unclear FAT scope, SIL proof test, third-party witness | +5–10% |
| Foreign exchange (FX) | Import components priced in USD/EUR, AUD fluctuation | +3–8% |
| Schedule compression | Rush manufacture, overtime, expedite freight | +10–20% |
| Site conditions | Remote location, offshore, extreme climate | +10–30% |
| Regulatory compliance | Changing standards, certification authority requirements | +5–15% |

## 3.2 Risk Register Template

| # | Risk Description | Probability (1–5) | Impact (1–5) | Risk Score (P×I) | Mitigation | Contingency ($) |
| --- | --- | --- | --- | --- | --- | --- |
| R01 | I/O list finalised 30% only – scope creep likely | 4 | 4 | 16 (HIGH) | Caveat in quote; rate per additional I/O point | 10% of PLC panel |
| R02 | Siemens S7-1500 lead time 20 weeks | 3 | 4 | 12 (HIGH) | Place CPU order immediately on award | $0 – manage with early PO |
| R03 | ATEX certification first-time for this panel type | 3 | 3 | 9 (MED) | Engage certifying body early; allow extra test hours | 5% of panel cost |
| R04 | Client may request additional FAT day | 2 | 2 | 4 (LOW) | Exclude extra FAT days from base scope; rate available | $2,500 per day |
| R05 | USD exchange rate movement on imported VFDs | 3 | 3 | 9 (MED) | FX hedge or quote FX variation clause | 3% of VFD cost |

## 3.3 Contingency vs Risk Allowance

- Contingency: A fixed percentage added to cover unknown or undefined scope elements

- Risk Allowance: A specific dollar amount added for identified, quantified risks

- Contingency is typically 5–15% on well-defined scope, 15–30% on early-stage estimates

- Risk allowances are itemised separately so they can be removed if the risk is resolved

- On competitive tenders, risk pricing must be competitive – over-contingencing loses bids

## 3.4 Estimation Confidence Levels

| Estimate Class | Stage | Scope Definition | Accuracy Range | Contingency |
| --- | --- | --- | --- | --- |
| Class 5 – Order of Magnitude | Concept / pre-FEED | 0–2% | -50% to +100% | 30–50% |
| Class 4 – Budgetary | Pre-FEED / FEED | 1–15% | -30% to +50% | 20–30% |
| Class 3 – Preliminary | FEED / early detailed | 10–40% | -20% to +30% | 15–20% |
| Class 2 – Definitive | Detailed design | 30–75% | -10% to +20% | 10–15% |
| Class 1 – Final (Tender) | Complete documents | 65–100% | -5% to +10% | 5–10% |

# 4. Lifecycle Cost Analysis (LCC) & Value Engineering

## 4.1 Total Cost of Ownership (TCO)

Clients increasingly evaluate panel purchases on total cost of ownership, not just purchase price. An estimator who can demonstrate low lifecycle cost gains a competitive advantage.

| Cost Phase | Cost Elements | Notes |
| --- | --- | --- |
| Capital Cost (CAPEX) | Panel purchase, installation, commissioning, project management | What most estimates focus on |
| Energy Cost (OPEX) | Losses in drives (efficiency), transformer losses, cooling power | VFDs save 30–60% energy on variable speed loads |
| Maintenance Cost (OPEX) | Scheduled maintenance, spare parts holding, service contracts | Withdrawable MCCs reduce maintenance downtime |
| Downtime Cost | Production loss during unplanned outages, MTTR (mean time to repair) | Redundant systems have higher CAPEX but lower downtime cost |
| End of Life Cost | Decommissioning, disposal, hazardous material management | ATEX panels may require specialist decommissioning |

## 4.2 VFD Energy Savings Calculation

This is a powerful sales tool. Variable torque loads (pumps, fans) follow the affinity laws:

- Flow is proportional to speed: Q ∝ N

- Head/pressure is proportional to speed squared: H ∝ N²

- Power is proportional to speed cubed: P ∝ N³

Energy Savings Example Calculation

A 75kW pump motor running at 100% speed 24/7 at $0.15/kWh costs approximately $98,550/year in energy. If reduced to 80% speed using a VFD, power reduces to 75kW × 0.8³ = 75 × 0.512 = 38.4kW. Annual energy cost = $50,371/year. Annual saving = $48,179. A VFD panel for this motor may cost $18,000–25,000, giving a payback of less than 6 months. Present this LCC analysis to justify VFD over DOL.

## 4.3 Value Engineering Techniques

Value engineering (VE) is the systematic analysis of a design to achieve required functions at the lowest cost. For panel estimation, key VE techniques include:

| VE Technique | Description | Typical Saving |
| --- | --- | --- |
| Alternative brand substitution | Propose equivalent brand where specification permits alternatives | 10–30% on components |
| Standardise enclosure sizes | Use standard catalogue sizes rather than custom fabrication | 15–25% on enclosure cost |
| Combine small panels | Merge two small PLC panels into one larger enclosure | Reduce enclosure + wiring cost |
| Reduce IP rating | Where environment permits, IP31 vs IP54 saves cost | 10–20% on enclosure |
| Simplify bypass circuit | Manual bypass vs auto-changeover bypass | 5–10% on VFD panel |
| Reduce spare I/O | 20% spare vs 25% spare where scope is well-defined | 1–2 fewer modules |
| Use remote I/O instead of home-run cabling | Ethernet/Profinet remote I/O reduces cable cost on large sites | Variable – high savings on large plants |
| Standard off-the-shelf components | Avoid specifying obsolete or rare components | Reduces procurement risk and cost |
| Modular / standard designs | Use existing panel designs rather than custom for each project | 15–25% on engineering hours |

# 5. Specialist Panel Types

## 5.1 ATEX / IECEx Hazardous Area Panels

Hazardous area panels are required where flammable gases, vapours, dusts, or fibres may be present. The ATEX/IECEx certification system ensures equipment cannot ignite the atmosphere.

| Zone Classification | Description | Equipment Category Required |
| --- | --- | --- |
| Zone 0 (Gas) | Explosive atmosphere present continuously | Category 1G – very rare in panels |
| Zone 1 (Gas) | Explosive atmosphere present occasionally during normal operation | Category 2G – Ex d, Ex e, Ex p enclosures |
| Zone 2 (Gas) | Explosive atmosphere not likely in normal operation | Category 3G – Ex n, Ex e, Ex p enclosures |
| Zone 20 (Dust) | Explosive dust cloud present continuously | Category 1D |
| Zone 21 (Dust) | Explosive dust cloud present occasionally | Category 2D |
| Zone 22 (Dust) | Explosive dust cloud not likely in normal operation | Category 3D |

### ATEX Panel Protection Methods

- Ex d (Flameproof): Enclosure withstands internal explosion and prevents external ignition – very robust, heavy, expensive

- Ex e (Increased Safety): Enhanced construction to prevent sparks/arcs in normal operation – common for terminals, junction boxes

- Ex p (Pressurisation): Enclosure purged with clean air/inert gas to prevent ingress of hazardous atmosphere – used for large PLC/VFD panels in Zone 1

- Ex n (Non-incendive): Non-sparking in normal operation – Zone 2 only

- Ex ia/ib (Intrinsic Safety): Limits energy in circuit to non-igniting level – used for field instruments, sensors

ATEX Estimation Warning ATEX/IECEx certification is a specialist field. Standard VFDs and PLCs cannot be used in Zone 1 without Ex p pressurisation system. The pressurisation unit (purge & pressurisation controller) adds $5,000–$25,000 per panel. All components inside must be suitable for use inside a purged enclosure. Engage a certified Ex panel manufacturer early in the estimate process. Never attempt to estimate an ATEX panel without specialist input.

## 5.2 Functional Safety – SIL-Rated PLC Systems

Safety Instrumented Systems (SIS) are designed to bring a process to a safe state when predetermined conditions are violated. They are rated by Safety Integrity Level (SIL) per IEC 61511.

| SIL Level | Risk Reduction Factor | Probability of Failure on Demand (PFD) | Typical Application |
| --- | --- | --- | --- |
| SIL 1 | 10 – 100x | 0.1 to 0.01 | Low-risk process upsets, pump protection |
| SIL 2 | 100 – 1000x | 0.01 to 0.001 | Process plant ESD, pressure relief bypasses |
| SIL 3 | 1000 – 10,000x | 0.001 to 0.0001 | Offshore ESD, toxic chemical containment |
| SIL 4 | >10,000x | <0.0001 | Nuclear, aviation – rarely in industrial panels |

### SIL System Estimation Premium Items

- SIL-rated PLC hardware (e.g., Siemens S7-1500F, Allen Bradley GuardLogix) – 50–100% premium over standard

- Redundant CPU architecture (1oo2 or 2oo3 voting logic) – doubles or triples processor cost

- SIL-rated I/O modules – specialised modules with diagnostics and self-test

- Functional safety engineer (FSE) – dedicated safety lifecycle management resource

- Safety Requirements Specification (SRS) development – engineering deliverable

- FMEA / LOPA analysis – safety analysis to verify SIL level achieved

- Third-party safety certification (TUV, Bureau Veritas) – additional cost and time

- Proof test procedure development and execution – required every 1–5 years

## 5.3 Marine & Offshore Panels

Marine panels are subject to classification society rules (DNV, ABS, Lloyd's Register, Bureau Veritas) and the harsh marine environment.

- Vibration resistance: Components must survive vessel motion, wave-induced vibration

- Corrosion protection: Stainless steel, marine-grade coatings, conformal coated PCBs

- IP rating: Minimum IP44 for interior marine, IP56 for weather-exposed locations

- EMC compliance: Particularly strict on vessels due to sensitive navigation equipment

- Classification approval: All equipment must be approved by the relevant class society

- Inclination tolerance: Panels must operate at up to 22.5° list and 10° trim

- Slamming loads: Equipment secured against wave slamming g-forces

# 6. Commercial & Contract Management

## 6.1 Contract Types

| Contract Type | Description | Risk to Supplier | When Used |
| --- | --- | --- | --- |
| Lump Sum (Fixed Price) | Agreed fixed price for defined scope | HIGH – supplier absorbs cost overruns | Well-defined scope, competitive tender |
| Reimbursable (Cost Plus) | Actual cost + agreed fee/margin | LOW – client absorbs cost risk | Early FEED, undefined scope |
| Schedule of Rates (SOR) | Fixed unit rates, variable quantities | MEDIUM – unit rate risk | Repetitive work, uncertain quantity |
| Target Cost | Agreed target; gain/pain share above/below | MEDIUM – shared risk | Alliance contracts, collaborative projects |
| EPC (Engineering, Procurement, Construction) | Turnkey – all phases at fixed price | VERY HIGH | Major capital projects, strong contractor |

## 6.2 Contract Key Clauses for Panel Suppliers

- Scope of work: Ensure all inclusions and exclusions are clearly defined

- Variations / change orders: Process for pricing and approving scope changes

- Payment terms: Progress payments vs milestone payments; retention (typically 5–10%)

- Liquidated damages (LDs): Penalty for late delivery – often $500–$5,000/day; always cap LD exposure

- Intellectual property: Who owns panel designs, software, and documentation

- Warranty: Duration (typically 12–24 months from commissioning), scope, response time

- Force majeure: Relief from delays caused by events outside control (pandemic, natural disaster)

- Governing law: Which jurisdiction's law applies to the contract

## 6.3 Variations & Change Management

Variations (also called change orders) are formal contract amendments that adjust scope, price, or schedule. Managing variations is critical to project profitability.

- Variation trigger: Client requests additional scope, specification changes, or conditions differ from what was tendered

- Variation process: Identify change → assess impact (cost + time) → submit variation request → client approval → implement

- Pricing a variation: Use the same methodology as the original estimate (BOM + labour) – document thoroughly

- Time impact: Always assess if the variation affects the critical path and claim extension of time if applicable

- Back-charge: Supplier may issue back-charge to client for costs incurred due to client-caused delays

Commercial Insight

Variations are a significant source of project margin for panel suppliers. A well-managed variation process can add 10–20% to original contract value on complex projects. However, poorly managed variations (not submitted, not approved in writing, or submitted too late) can result in cost absorption. Always submit variations in writing immediately when a change is identified. Never do extra work without written approval.

## 6.4 Retention & Payment Management

| Payment Milestone | Typical % | Trigger Event |
| --- | --- | --- |
| Order acknowledgement / mobilisation | 10–20% | Purchase order received and acknowledged |
| Long-lead item procurement | 20–30% | VFD / PLC orders placed with vendor |
| Panel build completion | 30–40% | Panel assembly complete, ready for FAT |
| FAT completion | 10–15% | FAT successfully completed and signed off |
| Delivery to site | 5–10% | Panel delivered and received by client |
| Retention release | 5–10% | Retention released after defects liability period |

# 7. Advanced Estimation Tools & Technology

## 7.1 Estimation Software

| Software / Tool | Type | Key Features | Used For |
| --- | --- | --- | --- |
| Microsoft Excel | Spreadsheet | BOM templates, pricing, labour schedules | Most common estimation tool |
| Procore / Aconex | Project management | Document control, variation management, RFI tracking | Large EPC projects |
| EPLAN Electric P8 | CAD / Engineering | Automated BOM generation from schematics, parts database | Engineering-driven estimates |
| SEER-H / Sage Estimating | Dedicated estimation | Database of historical rates, automated labour pricing | Formal cost estimating |
| Oracle Primavera P6 | Scheduling | Project schedule, resource loading, critical path | Schedule-linked estimates |
| SAP / Oracle ERP | Enterprise | Integrated BOM, procurement, actual cost tracking | Large organisations |
| Power BI / Tableau | Data visualisation | Estimate vs actual analysis, margin reporting | Estimation analytics |

## 7.2 Developing Estimation Databases

A well-maintained estimation database is a competitive advantage. It should contain:

- Historical project actuals: Compare estimated vs actual cost and hours for each panel type

- Material price book: Current buy prices for frequently used components, updated quarterly

- Labour rate schedule: Current award rates by trade, including oncosts and overhead

- Vendor lead time database: Current lead times by component category, updated monthly

- Standard panel templates: Pre-priced standard panel types (e.g., '22kW DOL starter panel', '100 I/O PLC panel')

- Correction factors: Climate derating, ATEX premium, SIL premium, stainless premium

## 7.3 Estimate Benchmarking & Sanity Checks

Before submitting any estimate, perform the following benchmarking checks:

- Cost per I/O point: Total PLC panel cost divided by total I/O count (typical: $800–$2,500/I/O point depending on complexity)

- Cost per kW (VFD): Total VFD panel cost divided by drive kW rating (typical: $200–$800/kW depending on rating and IP)

- Cost per motor starter unit (MCC): Total MCC cost divided by number of starters (typical: $1,500–$8,000 per starter depending on kW and type)

- Labour % of total: Labour should typically be 20–35% of total panel cost – if outside this range, investigate

- Material : Labour ratio: Compare to similar historical projects in your database

- Cross-check with order-of-magnitude budget estimates if available from client

# 8. International Projects & Export Considerations

## 8.1 Export Project Complexity Factors

- Shipping: Sea freight (FCL, LCL, flat-rack for large panels), packing standards (ISPM-15 for timber), insurance

- Customs & duties: Import tariffs, duty drawback, HS codes for electrical equipment

- Voltage & frequency: Confirm project site voltage and frequency (60Hz in Americas, some Asian countries)

- Standards: IEC vs NEMA/UL; some countries mandate local standards (e.g., Brazilian NR-10, Indian IS standards)

- Language: Documentation may need to be in local language (nameplate labelling, manuals)

- Currency: Quote in USD/EUR or local currency – include FX risk allowance

- Climate: Design for local ambient conditions (Middle East: 55°C, tropical: high humidity, arctic: -40°C)

## 8.2 Incoterms for Panel Supply

| Incoterm | Delivery Point | Who Pays Freight/Insurance | Risk Transfer |
| --- | --- | --- | --- |
| EXW – Ex Works | Seller's factory | Buyer | At factory gate |
| FCA – Free Carrier | Named place (e.g., forwarder's depot) | Buyer (from named place) | At named place |
| FOB – Free on Board | Port of export, loaded on vessel | Buyer (ocean freight) | On board vessel |
| CIF – Cost Insurance Freight | Destination port | Seller pays freight + insurance | At destination port |
| DAP – Delivered at Place | Named destination | Seller pays all freight | At destination |
| DDP – Delivered Duty Paid | Named destination, duty paid | Seller pays all incl. import duty | At destination |

## 8.3 Foreign Currency Risk Management

- Identify all imported components priced in foreign currency (USD: US drives/PLC; EUR: German brands)

- Obtain FX forward rate from treasury/finance at time of tender submission

- Include FX variation clause in quotation if project duration exceeds 90 days

- Alternatively, add FX contingency (typically 3–8% on imported content)

- For large projects, consider hedging strategy with finance team

# 9. Quality Assurance & Documentation in Estimation

## 9.1 Quality Inspection & Test Plan (ITP)

An Inspection and Test Plan (ITP) is a document that defines the quality hold points and witness points for panel manufacturing. The ITP has a direct cost impact as each hold point requires inspection time and documentation.

| ITP Stage | Activity | Who Witnesses | Documentation |
| --- | --- | --- | --- |
| Material receiving inspection | Check incoming components against PO and BOM | Internal QA | Receiving report, NCR if failed |
| In-process inspection | Check wiring in progress against drawings | Internal / third party | Inspection checklist sign-off |
| Routine test (pre-FAT) | Full electrical test before FAT | Internal test technician | Test report |
| FAT – Hold Point | Client/third party must witness – work cannot proceed without sign-off | Client + third party | FAT sign-off, punchlist |
| Final inspection | Final visual and documentation check | Internal QA + client | Final acceptance certificate |
| Packing and shipping inspection | Verify packing, loading, dunnage | Client or freight forwarder | Packing list, BL, photos |

## 9.2 As-Built Documentation Suite

The documentation deliverables are a significant and often underestimated cost element. A typical panel documentation suite includes:

- General Arrangement (GA) drawing: Enclosure dimensions, door arrangement, weights, lifting points

- Component layout drawing: Physical location of each component on mounting plate

- Single line diagram (SLD): Power distribution schematic for MCC/VFD panels

- Schematic (wiring diagram): Detailed circuit-by-circuit wiring diagram

- Termination drawings: Terminal block schedules, cable and core numbering

- I/O schedule: Complete list of all PLC I/O with instrument tag, module address, and signal type

- Bill of Materials (as-built): Confirmed BOM with actual part numbers installed

- Test report: FAT test results, calibration certificates

- Operation & Maintenance manual: Component data sheets, maintenance schedules, troubleshooting guide

- Software backup: PLC program backup (USB/CD), version controlled

Documentation Cost Rule of Thumb

Documentation typically represents 5–12% of a panel project's total cost. For ATEX, SIL, or marine certified panels, documentation requirements are significantly more extensive and may represent 15–20%. Always itemise documentation as a separate line in your estimate – it is real cost and should not be absorbed into other items.

# 10. Capstone Project – Advanced Estimation Exercise

## 10.1 Scenario Description

You are the lead estimator for a mining process plant expansion project. The client has issued a Request for Quotation (RFQ) for the following panel scope:

| Item | Description | Qty |
| --- | --- | --- |
| MCC-01 | 400V Main Motor Control Centre – Form 4b, Withdrawable, IP54, 2000A Incomer, 22 motor starter units (mix of DOL, SD, and VFD fed) | 1 No. |
| VFD-01 to VFD-04 | VFD panels for 4x conveyor drives: 2x 75kW, 1x 132kW, 1x 200kW. IP54, with bypass, Profinet comms, braking resistor | 4 No. |
| PLC-01 | Siemens S7-1500 PLC panel, 320 DI, 180 DO, 85 AI, 40 AO, 25% spare, Profinet, Profibus DP, UPS, Panel PC 21" | 1 No. |
| E-HOUSE-01 | 20ft ISO E-House to house MCC-01, PLC-01, marshalling racks. Includes A/C, lighting, fire detection, earthing | 1 No. |

## 10.2 Exercise Requirements

- Develop a preliminary BOM for each panel type (minimum 15 line items per panel)

- Estimate total I/O module count for PLC-01 (show all calculations with spare capacity)

- Calculate total VFD heat dissipation for all four VFD panels and recommend cooling solution

- Develop a risk register with minimum 6 risks for this project scope

- Prepare a high-level labour estimate for the full project scope

- Identify five specification items that would most significantly increase cost if required

- Prepare an executive summary of the estimate suitable for review by the Sales Manager

## 10.3 Exercise Assessment Criteria

| Assessment Area | Marks | Key Evaluation Points |
| --- | --- | --- |
| BOM completeness and accuracy | 25 | No major omissions, correct specifications, reasonable quantities |
| I/O calculation methodology | 15 | Correct calculation, appropriate spare capacity, correct module grouping |
| Thermal management analysis | 10 | Correct heat load calculation, appropriate cooling solution selected |
| Risk register quality | 15 | Risks identified, probability/impact assessed, mitigations proposed |
| Labour estimate methodology | 15 | Reasonable hours, appropriate labour categories, multipliers applied |
| Commercial awareness | 10 | Spec risks identified, exclusions flagged, assumptions documented |
| Presentation quality | 10 | Clear, professional, readable executive summary |

# 11. Career Development – Advanced Skills for GET Engineers

## 11.1 Technical Skills Roadmap

| Timeframe | Skills to Develop | How to Develop |
| --- | --- | --- |
| Month 1–3 (GET) | Panel fundamentals, BOM development, basic estimation | Structured training (Weeks 1–3), shadowing senior estimators |
| Month 4–6 | Lead small panel estimates independently, read specs unaided | Own estimates with senior review; attend supplier/vendor presentations |
| Month 7–12 | Multi-panel system estimates, FAT participation, variation pricing | Participate in full project lifecycle from quote to delivery |
| Year 2 | Complex estimates, SIL/ATEX exposure, client interaction | Lead estimates on complex projects with guidance |
| Year 3+ | Estimation team leadership, strategy, key account management | Formal project management or commercial training |

## 11.2 Professional Development & Qualifications

- Engineers Australia membership (MIEAust) – maintain CPD log with estimation activities

- AIPM (Australian Institute of Project Management) – project management fundamentals

- TIA (The Institute of Estimating) – formal cost engineering qualifications

- Vendor training: Siemens TIA Portal, Allen Bradley Studio 5000, ABB Drive training

- EPLAN Electric P8 training – schematic design and BOM generation

- Functional Safety Engineer (FSE) training – IEC 61508/61511 (TUV approved course)

- ATEX awareness training – awareness level certification for hazardous area panels

## 11.3 Key Professional Habits for Estimators

- Document all assumptions – every estimate should have a clearly written basis of estimate (BOE)

- Maintain a lessons learned log – record what was under or over-estimated on every project

- Stay current on component pricing – check vendor price books quarterly

- Build vendor relationships – strong relationships with key suppliers give you better pricing and lead time information

- Attend industry events – Austech, ARBS, Mining Expo – to understand new technology and products

- Read specifications thoroughly – one missed specification clause can cost a project its margin

- Always get a second review – have a colleague check your estimate before submission

# 12. Week 3 Advanced Glossary

| Term | Definition |
| --- | --- |
| ALARP | As Low As Reasonably Practicable – risk management principle for safety systems |
| ATEX | ATmosphères EXplosibles – EU directive for equipment used in explosive atmospheres |
| BOE | Basis of Estimate – document recording all assumptions underlying a cost estimate |
| CAPEX | Capital Expenditure – one-time costs for acquiring or building assets |
| DDP | Delivered Duty Paid – Incoterm where seller bears all costs to named destination |
| EPC | Engineering, Procurement, Construction – turnkey contract type |
| ESD | Emergency Shutdown – safety system designed to initiate a safe shutdown of process |
| E-House | Electrical House – prefabricated modular building housing electrical equipment |
| Ex d | Flameproof ATEX protection method – enclosure withstands internal explosion |
| Ex e | Increased Safety ATEX protection – enhanced construction to prevent arcs |
| Ex ia/ib | Intrinsic Safety – limits circuit energy to non-igniting levels for Zone 0/1 |
| Ex p | Pressurisation ATEX protection – enclosure purged with clean air or inert gas |
| FCL / LCL | Full Container Load / Less than Container Load – sea freight modes |
| FMEA | Failure Mode and Effects Analysis – systematic identification of failure modes and impacts |
| FX | Foreign Exchange – currency exchange rate between two currencies |
| IECEx | International IEC Explosive Atmospheres – international certification scheme |
| Incoterms | International Commercial Terms – standard trade terms defining delivery and risk |
| ITP | Inspection and Test Plan – document defining quality hold and witness points |
| LCC | Lifecycle Cost Analysis – evaluation of cost over entire asset lifetime |
| LD | Liquidated Damages – pre-agreed compensation for contractor delay |
| LOPA | Layer of Protection Analysis – quantitative method for assessing SIL levels |
| OPEX | Operating Expenditure – ongoing operational costs (energy, maintenance, labour) |
| PFD | Probability of Failure on Demand – key SIL metric; how often safety function fails when demanded |
| SIL | Safety Integrity Level – IEC 61511 classification for safety system integrity (1–4) |
| SIS | Safety Instrumented System – system designed to bring process to safe state on demand |
| SRS | Safety Requirements Specification – document defining functional safety requirements |
| TCO | Total Cost of Ownership – all costs over full life of asset, not just purchase price |
| TUV | Technischer Uberwachungsverein – German technical inspection association; SIL certifier |

End of Week 3 Advanced Study Document

Prepared for GET Estimation & Costing Engineer Training Program  |  Advanced: Complex Estimation, Risk, Commercial & Project Management