WEEK 1

STUDY DOCUMENT

GET Estimation & Costing Engineer

PLC Panels  |  VFD Panels  |  MCC Panels

| Role GET – Estimation & Costing Engineer | Week Week 1 – Induction | Topics PLC / VFD / MCC Panel Fundamentals |
| --- | --- | --- |

# 1. Introduction & Learning Objectives

Welcome to the GET (Graduate Engineer Trainee) Estimation and Costing program. This Week 1 study document covers the fundamental knowledge required to understand, estimate, and cost three critical industrial panel systems: Programmable Logic Controller (PLC) Panels, Variable Frequency Drive (VFD) Panels, and Motor Control Centre (MCC) Panels.

## 1.1 Learning Objectives

- Understand the purpose and construction of PLC, VFD, and MCC panels

- Identify key components and their functions within each panel type

- Learn the cost drivers and estimation parameters for each panel

- Understand relevant standards, specifications, and compliance requirements

- Develop the ability to read and interpret panel schedules and BOMs

- Apply estimation techniques used in industrial projects

## 1.2 Week 1 Study Plan Overview

| Day | Topic | Focus Area | Duration |
| --- | --- | --- | --- |
| Day 1 | MCC Panel Fundamentals | Components, types, standards | 8 hrs |
| Day 2 | VFD Panel Fundamentals | Drive selection, harmonics, cooling | 8 hrs |
| Day 3 | PLC Panel Fundamentals | I/O, processors, architecture | 8 hrs |
| Day 4 | Estimation Methods | BOM, cost drivers, quoting process | 8 hrs |
| Day 5 | Review & Assessment | Mock estimation exercise | 8 hrs |

# 2. Motor Control Centre (MCC) Panels

A Motor Control Centre (MCC) is an assembly of one or more enclosed sections containing power bus and motor control units. MCCs are used to centralize the electrical control of motors and associated equipment in industrial plants.

## 2.1 What is an MCC?

An MCC consolidates motor starters, protection devices, metering, and control wiring into a standardized, pre-engineered enclosure. It provides a safe, efficient means of distributing power to multiple motors from a single location.

Key Fact for Estimation

MCC panels are typically quoted per functional unit (cubicle/drawer). A standard MCC project includes incoming feeder, bus bar system, individual motor starter units, and instrumentation. Always identify the total number and rating of motor starter units early in estimation.

## 2.2 MCC Types & Forms of Separation

| Type/Form | Description | Application | Cost Impact |
| --- | --- | --- | --- |
| Form 1 | No separation between units; open bus | Light industrial, low budget | Base cost |
| Form 2b | Bus bars separated from functional units | General industry | +10–15% |
| Form 3b | Bus bars + terminals separated | Process industry standard | +20–30% |
| Form 4b | Full separation of all units & terminals | Critical / hazardous areas | +40–60% |
| Fixed Type | Non-withdrawable components | Simple applications | Lower cost |
| Withdrawable | Draw-out modules for live maintenance | Continuous process plants | +25–40% |

## 2.3 Key MCC Components

### 2.3.1 Incoming Section

- Main incomer MCCB/ACB – rated for full panel fault current

- Current Transformers (CTs) for metering

- Voltage Transformers (VTs) if required

- Power factor correction capacitors (if specified)

- Surge protection devices (SPDs)

### 2.3.2 Bus Bar System

- Horizontal main bus bar – copper or aluminium (rated kA)

- Vertical distribution bus bars per section

- Neutral bus bar

- Earth bus bar (continuous throughout panel)

### 2.3.3 Motor Starter Units

| Starter Type | Motor Range (kW) | Components | Typical Use |
| --- | --- | --- | --- |
| DOL (Direct on Line) | Up to 7.5 kW | Contactor + Overload relay + CB | Small pumps, fans |
| Star-Delta | 7.5 – 45 kW | 3 contactors + timer + overload | Compressors, large fans |
| Soft Starter | 11 – 200 kW | Electronic soft starter + bypass | Conveyors, mixers |
| VFD Fed Unit | 0.75 – 1000+ kW | Contactor + fuses + VFD | Variable speed loads |
| Reversing Starter | 0.75 – 45 kW | 2 contactors + interlock + O/L | Hoists, gate valves |

## 2.4 MCC Panel Standards

- IEC 61439-2: Low-voltage switchgear and controlgear assemblies

- AS/NZS 3439.1: Low voltage switchgear assemblies (Australian standard)

- NEMA ICS 18: Motor Control Centres (North American)

- IEC 60529: Degrees of protection (IP ratings)

- IEC 60947: Low-voltage switchgear and controlgear

## 2.5 MCC Estimation Parameters

The following parameters are critical inputs for accurate MCC estimation:

| Parameter | Description | Where to Find |
| --- | --- | --- |
| Motor Schedule | List of all motors, kW ratings, starting method | P&ID / Motor Schedule |
| Voltage & Frequency | LV system voltage (415V / 480V), 50/60Hz | Electrical SLD |
| Fault Level (kA) | Prospective short circuit current at incomer | Power system study |
| IP Rating | Ingress protection requirement (IP31, IP54, IP65) | Specification |
| Form of Separation | Form 1 to Form 4b | Specification |
| Withdrawable/Fixed | Module type required | Specification |
| Control Voltage | 24VDC, 110VAC, 240VAC for control circuits | Control philosophy |
| SCADA/BMS Interface | Digital I/O, Profibus, Modbus, Ethernet | Control philosophy |
| Metering Requirements | Power meters, energy metering per circuit | Specification |
| Cable Entry | Top/bottom entry, gland size, number of cables | Cable schedule |

# 3. Variable Frequency Drive (VFD) Panels

A Variable Frequency Drive (VFD) panel houses one or more electronic drive units that control the speed and torque of AC induction motors by varying the frequency and voltage of the supply. VFDs provide significant energy savings (up to 50%+) on variable torque loads such as fans and pumps.

## 3.1 How a VFD Works

A VFD converts fixed frequency AC power to variable frequency AC through three stages:

- Rectifier Stage: Converts AC to DC using a diode bridge or active front end (AFE)

- DC Bus / Filter: Smooths the DC using capacitors and inductors

- Inverter Stage: Converts DC back to variable frequency/voltage AC using IGBTs (Insulated Gate Bipolar Transistors)

Estimation Tip

Always check if the specification calls for a standard 6-pulse drive or a 12-pulse/18-pulse or Active Front End (AFE) drive. Harmonic mitigation requirements can increase panel cost by 30–100% per drive unit. Confirm IEEE 519 or AS/NZS 61000 compliance requirement.

## 3.2 VFD Panel Components

| Component | Function | Cost Note |
| --- | --- | --- |
| VFD / Inverter Unit | Core drive – converts power to variable frequency | Major cost driver (50–70% of panel) |
| Input Isolation Transformer | Galvanic isolation, reduces harmonics | Required on some specs (+15–25%) |
| Input Line Reactor (ACL) | Reduces harmonic current distortion | Common specification requirement |
| Output dV/dt Filter | Protects motor winding insulation | Required for long cable runs >50m |
| Input MCCB / Fuse Switch | Over-current protection for VFD | Standard item |
| Bypass Contactor (Auto/Manual) | Allows DOL operation if VFD fails | Common requirement (+10–15%) |
| Braking Resistor / Chopper | Dissipates regenerative energy | Required for high-inertia loads |
| EMC Filter | Reduces conducted EMI emissions | Required for CE/IEC compliance |
| Control Power Supply (24VDC) | Powers control card and I/O | Standard item |
| HMI / Keypad | Local speed control and diagnostics | Size and brand dependent |
| Terminal Blocks & Cabling | Field wiring connections | Labour-intensive in multi-drive panels |

## 3.3 VFD Selection Parameters

| Parameter | Importance | Impact on Estimation |
| --- | --- | --- |
| Motor kW / HP rating | Sizes the drive | Fundamental – determines frame size |
| Motor full load current (FLA) | Ensures drive is not undersized | Always add 10–20% service factor |
| Load type (CT vs VT) | Constant torque vs variable torque | CT rating costs more for same kW |
| Overload requirement (%) | 150% for 60s (CT), 110% for 60s (VT) | Determines drive current rating |
| Ambient temperature (°C) | Affects drive derating | May need larger frame / cooling |
| Altitude (m above sea level) | Derating above 1000m | Drive may need to be oversized |
| Protection class (IP) | IP20, IP21, IP54, IP66 | Higher IP = higher cost + size |
| Communication protocol | Profibus, Modbus, Ethernet/IP | Add fieldbus option card |
| Harmonic standard | IEEE 519, IEC 61000-3-12 | May require AFE or 12-pulse input |
| Braking requirement | Stop time, load inertia | May need braking resistor assembly |

## 3.4 VFD Panel Types

- Single Drive Panel: One VFD per enclosure – standard for large drives (>45kW)

- Multi-Drive MCC: Multiple VFD units in a common MCC structure – space efficient

- VFD + Bypass Panel: Drive with manual/auto bypass for critical duty applications

- Regenerative / 4-Quadrant: Active front end for regenerative loads (cranes, elevators, test rigs)

- Marine / Hazardous Area: ATEX/IECEx rated enclosures – specialty requirement

## 3.5 VFD Standards

- IEC 61800-5-1: Adjustable speed electrical power drive systems – safety requirements

- IEC 61800-3: EMC requirements for drive systems

- IEEE 519: Recommended practices for harmonic control (US/international)

- IEC 60529: IP protection ratings

- UL 508A: Industrial control panel standard (North American market)

# 4. PLC (Programmable Logic Controller) Panels

A PLC panel houses the programmable logic controller system, I/O modules, power supplies, and associated hardware required to automate and monitor industrial processes. The PLC panel is the 'brain' of the automation system, interfacing between field instruments, actuators, and the control room / SCADA system.

## 4.1 PLC System Architecture

- Field Level: Sensors, transmitters, limit switches, valve positioners

- Control Level: PLC processor + I/O modules (the PLC panel)

- Supervisory Level: SCADA / HMI / DCS (engineering workstations, servers)

## 4.2 PLC Panel Major Components

| Component | Description | Estimation Note |
| --- | --- | --- |
| CPU / Processor Module | Main logic processor – executes ladder/FBD program | Brand, scan speed, memory size matter |
| Power Supply Unit (PSU) | Converts 240VAC to 24VDC for PLC backplane | Redundant PSU adds cost |
| I/O Modules – DI | Digital Input – reads switch/contact signals (24VDC) | Qty driven by I/O schedule |
| I/O Modules – DO | Digital Output – drives relays, solenoids, indicators | Relay output vs transistor output |
| I/O Modules – AI | Analogue Input – 4–20mA, 0–10V, RTD, thermocouple | More expensive per channel than DI/DO |
| I/O Modules – AO | Analogue Output – 4–20mA to control valves, drives | Per channel cost |
| Communication Modules | Profibus DP, Profinet, Modbus TCP, EtherNet/IP | Protocol specific cards |
| Remote I/O Racks | I/O distributed near field devices via fieldbus | Reduces cable cost, adds hardware cost |
| UPS Module / Battery | Maintains PLC power during mains failure | Often specified for critical plants |
| Marshalling Terminal Blocks | Organises field cables to I/O modules | Labour-intensive – allow adequate time |
| Surge Protection (I/O SPDs) | Protects I/O from lightning and surges | Required in exposed or outdoor installs |
| Panel PC / HMI | Local human machine interface | Size and brand vary widely |
| Ethernet Managed Switch | Plant network connectivity, SCADA comms | Managed vs unmanaged cost difference |
| System Cabinets / Enclosure | Rittal, Hoffman, or equivalent 19" rack or custom | Stainless steel for hygienic/food grade |

## 4.3 Major PLC Brands & Platforms

| Brand / Platform | Common Range | Typical Market | Notes |
| --- | --- | --- | --- |
| Siemens S7-1200/1500 | Small to large | Process, infrastructure, OEM | TIA Portal programming environment |
| Allen Bradley (Rockwell) | MicroLogix to ControlLogix | Mining, food & bev, manufacturing | Studio 5000 Logix Designer |
| Schneider Modicon M340/M580 | Small to large | Water/wastewater, energy, process | Unity Pro / EcoStruxure |
| Mitsubishi iQ-R / FX | Micro to large | OEM, manufacturing, APAC | GX Works3 programming |
| Beckhoff TwinCAT | PC-based control | High speed, motion control | Software-based PLC on industrial PC |
| ABB AC500 | Modular | Power, process, infrastructure | Automation Builder platform |

## 4.4 I/O Count Methodology

The I/O count is the primary driver of PLC panel cost. The following steps are used to develop the I/O estimate:

- Step 1: Obtain the Instrument Index or P&ID and list all field instruments

- Step 2: Classify each instrument as DI, DO, AI, or AO

- Step 3: Apply a spare capacity allowance (typically 20–25% spare I/O per type)

- Step 4: Group I/O into module sizes (8, 16, or 32 channel modules)

- Step 5: Calculate number of racks/subbases required

- Step 6: Confirm processor capacity (max I/O per CPU backplane)

Key Estimation Formula

Total DI Modules = CEILING((Active DI Count × 1.25) / Module Channel Count) Apply same formula for DO, AI, AO separately. Processor selection must support the total I/O count with headroom for expansion.

## 4.5 PLC Panel Standards

- IEC 61131-1/2/3: Programmable controllers – general information, equipment, programming languages

- IEC 61508: Functional safety – for safety-rated PLCs (SIL rated systems)

- IEC 62443: Industrial network and system security

- AS/NZS 3000: Wiring rules (Australian/NZ installation standard)

- UL 508A: Industrial control panel standard (North American market)

- NEMA 250: Enclosure types standard

# 5. Estimation & Costing Fundamentals

As a GET Estimation and Costing Engineer, your primary role is to produce accurate, defensible cost estimates for panel supply and installation. This section outlines the estimation process and key cost drivers.

## 5.1 The Estimation Process

| Step | Activity | Output | Tools Used |
| --- | --- | --- | --- |
| 1 | Review client specification & drawings | Understanding of scope | PDF reader, redline notes |
| 2 | Develop Bill of Materials (BOM) | Component list with quantities | Excel / ERP |
| 3 | Source vendor prices | Material cost base | Vendor portals, price books |
| 4 | Calculate labour hours | Labour cost base | Labour rate schedule |
| 5 | Add overheads & margins | Estimated sell price | Pricing template |
| 6 | Compile estimate document | Formal quotation / estimate | Excel / Word / Estimation software |
| 7 | Review & approval | Approved estimate | Internal review checklist |
| 8 | Submit quotation | Customer quotation | PDF / email |

## 5.2 Key Cost Drivers by Panel Type

### MCC Panel Cost Drivers

- Total number of motor starter units and kW ratings

- Form of separation (Form 1 to Form 4b)

- Fixed vs withdrawable/draw-out modules

- Bus bar rating (A) and fault level (kA)

- IP rating and enclosure type (indoor vs outdoor/stainless steel)

- Number of metering and protection relays

- SCADA interface requirements and communication modules

### VFD Panel Cost Drivers

- Drive kW rating (the largest single cost element per unit)

- Brand and model specified (some specs name a preferred brand)

- Constant torque (CT) vs variable torque (VT) rating

- Harmonic mitigation requirement (12-pulse, AFE, filters)

- Bypass requirement (manual / auto / ATEX)

- IP rating – IP20 vs IP54 vs IP66 is significant cost difference

- Communication protocol and option cards required

### PLC Panel Cost Drivers

- Total I/O count (DI/DO/AI/AO breakdown)

- PLC platform / brand specified by client

- Safety integrity level (standard PLC vs SIL 2/3 rated system)

- Redundancy requirement (CPU redundancy, PSU redundancy)

- Number of communication interfaces and protocols

- UPS / battery backup requirement

- Panel PC / HMI screen size and specification

## 5.3 Typical Cost Structure (Indicative)

| Cost Element | MCC Panel (%) | VFD Panel (%) | PLC Panel (%) |
| --- | --- | --- | --- |
| Major components (starters/drives/PLC) | 35–45% | 55–70% | 40–55% |
| Enclosure & structural | 10–15% | 8–12% | 10–15% |
| Cabling & terminals | 8–12% | 5–8% | 12–18% |
| Secondary components (relays, MCBs etc.) | 10–15% | 5–10% | 8–12% |
| Labour – assembly & wiring | 20–30% | 12–20% | 20–30% |
| Testing & commissioning | 5–8% | 5–8% | 5–10% |
| Overhead & margin | 12–18% | 12–18% | 12–18% |

## 5.4 Estimation Red Flags – Things Not to Miss

- Cable entry requirements – gland plates, sealing, top vs bottom entry (cost impact on enclosure)

- Sun canopy / weatherproof hood for outdoor panels

- Type test certificate required (IEC 61439 verified testing adds cost)

- Factory Acceptance Test (FAT) – customer witnesses, adds prep and supervision time

- ATEX / IECEx certification for hazardous area panels – significant premium

- Hot dip galvanised or stainless steel enclosures for corrosive environments

- Painting / powder coat colour specification and thickness

- Witness of final acceptance test (FAT) at factory – travel cost for client

- Spares requirement – client may request installed spare modules

- As-built documentation, O&M manuals, and circuit diagram requirements

# 6. Reading & Interpreting Key Documents

## 6.1 Single Line Diagram (SLD)

The SLD shows the power distribution hierarchy from the main incomer through to individual loads. Key information to extract for estimation:

- System voltage (LV: 415V / 400V / 480V), frequency (50Hz / 60Hz)

- Main incomer rating (A) and fault level (kA) at MCC busbars

- Number and rating of outgoing feeders

- Location and rating of any transformers, capacitor banks

## 6.2 Motor Schedule / Equipment List

The motor schedule is the most critical document for MCC and VFD estimation. It should contain:

- Tag number (e.g., M-001, P-101A)

- Equipment description (e.g., Feed Pump No. 1)

- Motor kW rating and voltage

- Starting method (DOL, Star-Delta, VFD, Soft Starter)

- Duty classification (Continuous, Intermittent, Standby)

- Hazardous area classification (if applicable)

## 6.3 Instrument Index / I/O List

For PLC panel estimation, the instrument index / I/O list is the primary reference. Check for:

- Total count of each I/O type (DI, DO, AI, AO)

- Signal types for AI/AO (4–20mA, HART, RTD, Thermocouple, 0–10V)

- Any intrinsically safe (IS) circuits requiring IS barriers or galvanic isolators

- Any high-speed counter or encoder inputs requiring special modules

- Communication interfaces listed (Modbus, Profibus, Profinet, EtherNet/IP)

## 6.4 Technical Specification

The project technical specification defines the quality, standards, and specific requirements. Always read and highlight:

- Preferred or specified brands/models

- Required standards and certifications

- Environmental conditions (temperature, humidity, altitude, corrosive atmosphere)

- Testing requirements (routine tests, type tests, FAT, SAT)

- Documentation requirements (drawings, manuals, ITP)

# 7. Glossary of Key Terms

| Term | Definition |
| --- | --- |
| ACB | Air Circuit Breaker – used as main incoming protection in large MCCs |
| AFE | Active Front End – regenerative VFD input stage with low harmonics |
| AI/AO | Analogue Input / Analogue Output – continuous signal I/O (4-20mA typical) |
| BOM | Bill of Materials – itemised list of all components required |
| CT (load) | Constant Torque – load requiring full torque across full speed range |
| DI/DO | Digital Input / Digital Output – discrete on/off signal I/O |
| DOL | Direct on Line – simplest motor starting method, full voltage at startup |
| FAT | Factory Acceptance Test – witnessed testing at panel manufacturer's workshop |
| FLA | Full Load Amperes – rated motor current at full load |
| HMI | Human Machine Interface – touchscreen or panel-mounted display |
| IGBT | Insulated Gate Bipolar Transistor – switching device inside VFD inverter stage |
| IP Rating | Ingress Protection – IEC 60529 classification for dust and water resistance |
| kA | Kiloamperes – unit for fault current / short circuit current rating |
| MCCB | Moulded Case Circuit Breaker – protection device for feeders and starters |
| PLC | Programmable Logic Controller – industrial digital computer for automation |
| SAT | Site Acceptance Test – commissioning tests performed at site after installation |
| SIL | Safety Integrity Level – IEC 61508 classification for safety system reliability |
| SLD | Single Line Diagram – schematic showing power distribution hierarchy |
| SPD | Surge Protection Device – protects equipment from voltage transients |
| THD | Total Harmonic Distortion – measure of harmonic current/voltage distortion |
| UPS | Uninterruptible Power Supply – maintains power during mains failure |
| VFD | Variable Frequency Drive – electronic device controlling motor speed/torque |
| VT (load) | Variable Torque – load where torque requirement varies with speed (fans, pumps) |

End of Week 1 Study Document

Prepared for GET Estimation & Costing Engineer Training Program  |  PLC / VFD / MCC Panel Fundamentals