WEEK 2

STUDY DOCUMENT

GET Estimation & Costing Engineer

Panel Design  |  Detailed Specifications  |  Estimation Techniques

| Role GET – Estimation & Costing Engineer | Week Week 2 – Intermediate | Topics Design, Specs, Detailed Estimation |
| --- | --- | --- |

# 1. Week 2 Overview & Objectives

Week 2 builds on the foundational knowledge from Week 1. The focus shifts from understanding what panels are to how they are designed, specified, and estimated in detail. You will develop practical skills in creating Bills of Materials (BOM), applying labour rates, understanding panel layout and design constraints, and handling real-world estimation scenarios.

## 1.1 Week 2 Learning Objectives

- Create detailed Bills of Materials (BOM) for PLC, VFD, and MCC panels

- Understand panel mechanical design, layout, and thermal management

- Apply cable and busbar sizing principles to panel estimation

- Interpret and respond to technical specifications and deviations

- Understand factory testing (FAT) requirements and how to cost them

- Develop accurate labour hour estimates for panel assembly and wiring

- Understand vendor selection, procurement, and lead time management

## 1.2 Week 2 Study Plan

| Day | Topic | Key Activities | Duration |
| --- | --- | --- | --- |
| Day 1 | Panel Layout & Design | Enclosure sizing, component layout, thermal calc | 8 hrs |
| Day 2 | Cable & Busbar Sizing | Current ratings, derating, voltage drop calc | 8 hrs |
| Day 3 | Detailed BOM Development | BOM template, material take-off, vendor pricing | 8 hrs |
| Day 4 | Labour Estimation | Assembly hours, wiring hours, test hours | 8 hrs |
| Day 5 | Specification Compliance | Technical clarifications, deviations, risk register | 8 hrs |

# 2. Panel Mechanical Design & Layout

Before components can be priced, an estimator must understand how a panel is physically designed. The enclosure size, component layout, and thermal management directly affect the cost of the enclosure, installation, and any special cooling equipment.

## 2.1 Enclosure Selection

| Enclosure Type | Material | IP Rating | Typical Application | Relative Cost |
| --- | --- | --- | --- | --- |
| Sheet steel (powder coated) | 2mm mild steel | IP31–IP54 | Indoor general purpose | Base (1.0x) |
| Stainless steel 304 | 2mm SS304 | IP54–IP66 | Food, pharma, washdown | 2.5–3.5x |
| Stainless steel 316L | 2mm SS316L | IP54–IP66 | Marine, coastal, chemical | 3.5–5.0x |
| GRP/Fibreglass | Glass reinforced polymer | IP65 | Corrosive atmospheres, ATEX zones | 2.0–3.0x |
| Aluminium | 3mm aluminium | IP54 | Weight-critical, offshore | 2.0–2.5x |
| Cast iron (ATEX) | Cast iron | IP65–IP68 | Zone 1/2 hazardous area | 8–15x |

## 2.2 Enclosure Sizing Methodology

Enclosure dimensions must accommodate all components with adequate clearance for wiring, cable management, and maintenance access. Follow this sizing process:

- Step 1: List all components with their physical dimensions (H x W x D mm)

- Step 2: Calculate total din rail length required (allow 30% spare din rail space)

- Step 3: Calculate cable duct volume (allow 40% fill factor in ducts)

- Step 4: Add component mounting clearances (minimum 50mm between rows)

- Step 5: Add cable entry zone at bottom (minimum 200mm for gland plates)

- Step 6: Cross-check against manufacturer's standard enclosure catalogue sizes

- Step 7: Apply thermal check – total heat dissipation vs enclosure cooling capacity

Estimator Tip – Enclosure Sizing Rule of Thumb

For initial estimates, allow 1.5x the calculated component volume as the minimum enclosure internal volume. This accounts for cable management ducts, wiring clearances, spare space, and air circulation. Verify against detailed layout before final pricing.

## 2.3 Thermal Management

Heat generated by components inside a panel must be managed to prevent equipment damage and nuisance tripping. This is particularly critical for VFD panels.

| Component | Typical Heat Dissipation | Notes |
| --- | --- | --- |
| VFD (standard efficiency) | 2–3% of motor kW rating | E.g., 22kW drive dissipates ~500W |
| Soft Starter (during starting) | Heat pulse only – short duration | Usually does not require derating |
| DOL Motor Starter | 10–20W per starter unit | Negligible individually |
| PLC I/O Modules | 3–8W per module | Cumulative in large systems |
| PLC Power Supply | 10–30W | Depends on output current |
| Transformer (in-panel) | 2–5% of rated kVA | Significant – often needs ventilation |
| Control Power Supply 24VDC | 15–40W typical | Depends on load current |
| Indicating lamps / HMI | 2–20W | LED much lower than incandescent |

### Cooling Options

- Natural convection (louvres only): Suitable for low heat loads (<200W)

- Forced ventilation (fan + filter): Cost-effective for moderate heat loads (200–1000W)

- Air-to-air heat exchanger: Sealed enclosure, IP54/55 maintained, 500–2000W

- Air conditioner (panel AC unit): High heat loads >2kW, maintains low temperature

- Water-cooled cold plate: Specialist – high density VFD/power electronics

⚠ Common Estimation Mistake Forgetting to cost cooling equipment for VFD panels. A 22kW VFD in an IP54 enclosure will require a heat exchanger or panel air conditioner. Always calculate panel heat load and check if natural convection is adequate. A panel AC unit can add $1,500–$8,000 to a panel quote.

# 3. Cable & Busbar Sizing for Estimation

While detailed cable sizing is an engineering function, estimators need to understand the principles to correctly specify and cost cables, bus bars, and associated hardware.

## 3.1 Busbar Sizing Principles

Busbars in MCC panels must carry the full system load current plus fault current withstand capability.

| Parameter | Formula / Rule | Notes |
| --- | --- | --- |
| Current carrying capacity | I = P / (√3 × V × PF × η) | Full load current from total connected load |
| Busbar cross-section | Allow 1.6–2.0 A/mm² for copper busbars | Conservative design; derate for high ambient |
| Fault level withstand | I²t rating must exceed fault MVA × clearing time | Verified by power system study |
| Voltage drop | VD = I × R × L (single phase) / √3 for 3-phase | Should not exceed 1% on busbars |
| Busbar material | Copper: preferred; Aluminium: ~60% of copper capacity for same cross-section | Aluminium requires larger cross-section |
| Busbar insulation | Heat shrink sleeve or PVC insulation over bare bars | Required for Form 3b/4b separation |

## 3.2 Internal Panel Cable Types & Sizing

| Cable Type | Application | Size Range | Colour Coding (AS/IEC) |
| --- | --- | --- | --- |
| Power cable (PVC/PVC) | Motor feeder connections in MCC | 2.5 – 400mm² | Brown/Black/Grey + Green/Yellow Earth |
| Flexible control cable | Control wiring between components | 0.75 – 2.5mm² | Grey (control), Black (DC), Red (AC) |
| Screened cable | Analogue signals, encoder, fieldbus | 0.5 – 1.5mm² (pairs) | Grey with overall screen/drain wire |
| Fire rated cable (FP/LSZH) | Emergency circuits, evacuation systems | 1.5 – 16mm² | Red (fire), Orange (emergency) |
| Fibre optic | High-speed data, galvanic isolation | 2–24 core | Typically orange or yellow sheath |
| VFD output cable (shielded) | VFD to motor – reduces EMI | 4 – 400mm² | 3-core + earth + shield |

## 3.3 Cable Derating Factors

Cables derated for installation conditions. Estimators must flag if derating applies as it may require a larger (more expensive) cable:

- Ambient temperature above 30°C (40°C in Middle East/tropical climates – common derating 0.87)

- Cables grouped in bunches or conduit (bunching factor 0.7–0.9 depending on grouping)

- Cables in conduit or trunking vs free air (conduit factor ~0.77 for small sizes)

- Elevated altitude above 1000m (ambient temperature correction may still apply)

# 4. Developing a Detailed Bill of Materials (BOM)

The BOM is the foundation of every panel estimate. A complete, accurate BOM drives material cost, procurement schedule, and vendor enquiries. A poorly developed BOM leads to cost overruns and procurement delays.

## 4.1 BOM Structure

| BOM Field | Description | Example |
| --- | --- | --- |
| Item No. | Sequential reference number | 001, 002, 003... |
| Tag / Reference | Panel reference (matches drawing) | CB1, K1, T1, PSU1 |
| Description | Full technical description | MCCB 3P 63A 25kA Icu, Fixed, DIN mount |
| Manufacturer | Preferred or specified brand | Schneider Electric |
| Part Number | Manufacturer's catalogue number | LV432630 |
| Quantity | Number of units required | 3 |
| Unit | Unit of measure | Each / Metre / Set |
| Unit Price (ex GST) | Current buy price from vendor | $245.00 |
| Total Price | Qty × Unit Price | $735.00 |
| Lead Time | Procurement lead time (weeks) | 2–3 weeks |
| Remarks | Notes, alternatives, spec ref | Per spec clause 4.3.2 |

## 4.2 MCC Panel – Typical BOM Sections

- Section A: Enclosure & Structural (enclosure, panels, gland plates, back plates, DIN rail, cable duct, hardware)

- Section B: Incoming Section (ACB/MCCB, CTs, VTs, surge protection, energy meter, earth bar)

- Section C: Bus Bar System (copper bars, insulators, bus bar covers, bus bar joints)

- Section D: Motor Starter Units (contactors, overload relays, MCBs, pilot devices per starter)

- Section E: Control Wiring (terminal blocks, ferrules, labels, cable ties, control cable)

- Section F: Power Wiring (power cables, lugs, cable ties, glands, heat shrink)

- Section G: Instrumentation & Metering (power meters, ammeters, voltmeters, selector switches)

- Section H: Communication (Profibus card, Ethernet switch, fibre patch panels)

- Section I: Ancillaries (lighting, anti-condensation heater, thermostat, fan, door interlock)

## 4.3 VFD Panel – Typical BOM Sections

- Section A: Enclosure & Structure (enclosure, mounting plates, cable management, hardware)

- Section B: Input Protection (MCCB, fuse switch disconnector, surge protection)

- Section C: Input Conditioning (line reactor, isolation transformer, EMC filter)

- Section D: VFD Unit (drive module, option cards – fieldbus, I/O expansion, encoder)

- Section E: Output Section (output filter/reactor, motor thermistor relay, output contactor)

- Section F: Bypass Circuit (bypass contactor, interlock relay, manual selector switch)

- Section G: Braking (braking chopper, braking resistor assembly, temperature switch)

- Section H: Control & Instrumentation (24VDC PSU, terminal blocks, local stop/start)

- Section I: Cooling (panel fan, heat exchanger, panel AC unit, filter mats)

## 4.4 PLC Panel – Typical BOM Sections

- Section A: Enclosure & Structure (19" rack or custom enclosure, mounting rails, hardware)

- Section B: PLC Hardware (CPU module, backplane/rack, power supply, expansion racks)

- Section C: I/O Modules (DI modules, DO modules, AI modules, AO modules – quantities per type)

- Section D: Speciality I/O (high-speed counter, motion module, IS barrier, HART multiplexer)

- Section E: Communication (Profibus DP master, Profinet card, Modbus gateway, managed switch)

- Section F: Control Power (24VDC PSU, UPS module, battery module, distribution fuses)

- Section G: HMI / Visualisation (panel PC, touchscreen HMI, keyboard, monitor arm)

- Section H: Marshalling (terminal blocks, IS barriers, relay output modules, cable duct)

- Section I: Software (PLC programming software licence, SCADA licence, HMI runtime)

BOM Completeness Check

Before submitting an estimate, verify your BOM includes: (1) All consumables – cable ties, ferrules, heat shrink, loom clamps; (2) All hardware – screws, nuts, DIN rail end stops, mounting feet; (3) All labels – component labels, cable ferrules, nameplate; (4) Software licences; (5) Documentation – as-built drawings, O&M manuals, test reports. Missing consumables and documentation can add 3–8% to material cost.

# 5. Labour Hour Estimation

Labour is typically 20–35% of a panel's total cost. Accurate labour estimation requires knowledge of assembly and wiring methods, and a structured approach based on component counts and panel complexity.

## 5.1 Labour Categories

| Labour Category | Activities | Typical Rate (AUD/hr) |
| --- | --- | --- |
| Panel fabricator / metalworker | Enclosure modification, drilling, cutting, fitting back plates | $65–85 |
| Electrical assembler | DIN rail fitting, component mounting, cable duct installation | $70–90 |
| Electrical wirer (LV) | Control wiring, power wiring, ferrule fitting, terminating | $75–95 |
| Instrument technician | Analogue loop wiring, IS barrier installation, HART commissioning | $90–110 |
| Panel test technician | Routine testing, FAT preparation, insulation testing | $90–110 |
| Project engineer (supervision) | Design review, drawing issue, FAT management | $120–150 |
| Commissioning engineer | On-site commissioning, SAT, loop checks | $110–140 |

## 5.2 Labour Estimation by Panel Type

### MCC Panel Labour Benchmarks

| Activity | Labour Hours (per unit) | Notes |
| --- | --- | --- |
| Enclosure preparation (per section) | 4–8 hrs | Drilling, back plate fitting, cable duct |
| Bus bar installation (per section) | 3–6 hrs | Fitting, tightening, insulating, testing |
| DOL starter unit assembly & wiring | 3–5 hrs | Includes power and control wiring |
| Star-delta starter assembly & wiring | 5–8 hrs | Three contactors + interlock wiring |
| VFD feeder unit in MCC | 6–10 hrs | Includes VFD mounting and wiring |
| Instrumentation (per power meter/relay) | 2–4 hrs | Wiring to CTs, VTs, HMI |
| Terminal block wiring (per 10 terminals) | 1.5–2.5 hrs | Includes ferrule fitting and labelling |
| Routine test (per section) | 3–5 hrs | Continuity, insulation, operation test |
| FAT preparation (full MCC) | 8–16 hrs | Clean-up, documentation, cable dress |

### VFD Panel Labour Benchmarks

| Activity | Labour Hours | Notes |
| --- | --- | --- |
| Enclosure preparation | 2–4 hrs | Mounting plate, cable management |
| VFD mounting & power connections | 3–6 hrs | Scales with drive frame size |
| Input circuit (MCCB, reactor, filter) | 2–4 hrs | Depends on complexity |
| Bypass circuit assembly | 4–6 hrs | Two contactors + interlock + wiring |
| Control wiring & I/O termination | 3–5 hrs | Fieldbus card, start/stop, references |
| Braking resistor assembly (external) | 2–4 hrs | Resistor mounting, cable to panel |
| Drive commissioning & parameter setting | 2–4 hrs | Basic parameters, run test |
| FAT per drive panel | 2–4 hrs | Documentation + run test with load bank |

### PLC Panel Labour Benchmarks

| Activity | Labour Hours | Notes |
| --- | --- | --- |
| Enclosure preparation & DIN rail fitting | 3–5 hrs | Back plate, cable duct, rail |
| PLC hardware mounting (CPU + racks) | 2–3 hrs | Rack mounting, PSU connection |
| I/O module population (per 16ch module) | 0.5–1 hr | Insert, secure, label |
| Marshalling terminal wiring (per 100 I/O) | 15–25 hrs | Highest labour activity in PLC panel |
| IS barrier / isolator installation (per 10) | 3–5 hrs | Includes rail mounting + wiring |
| Communication module installation | 1–2 hrs per module | Physical + initial configuration |
| 24VDC power distribution wiring | 2–4 hrs | PSU output, distribution fuses, UPS |
| Cable management & dressing | 3–6 hrs | Tying, labelling, duct covers |
| PLC hardware checkout | 4–8 hrs | Power-on, I/O force test, comms check |
| FAT support (per day) | 8 hrs | Support client witness, punch list |

## 5.3 Labour Complexity Multipliers

Adjust base labour hours using these multipliers for project-specific conditions:

| Condition | Multiplier | Rationale |
| --- | --- | --- |
| Standard domestic specification | 1.0x (base) | Normal complexity |
| Overseas export / ATEX certification | 1.2–1.4x | Additional paperwork, inspection hold points |
| SIL-rated safety system | 1.5–2.0x | Rigorous testing, dual sign-off, proof test records |
| Hazardous area enclosure (cast iron, ATEX) | 1.3–1.5x | Specialised work, strict procedures |
| Rush / accelerated schedule | 1.2–1.5x | Overtime, reduced efficiency |
| Complex multi-drop fieldbus network | 1.2–1.3x | Commissioning, addressing, testing |
| Stainless steel hygienic panel (food/pharma) | 1.3–1.6x | Surface finish, passivation, cleaning |
| Retrofit / modification to existing panel | 1.4–1.8x | Work in live panel, isolation procedures |

# 6. Vendor Management & Procurement

## 6.1 Key Vendor Categories

| Vendor Category | What They Supply | Lead Time (typical) | Key Vendors |
| --- | --- | --- | --- |
| Enclosure manufacturer | Steel/SS enclosures, panels, cable duct | 2–6 weeks | Rittal, Hoffman, Stoddart, Metsel |
| Circuit protection | MCCBs, MCBs, fuses, ACBs, earth leakage | 1–4 weeks | Schneider, ABB, Eaton, Siemens |
| Contactors & overloads | Contactors, thermal overloads, motor starters | 1–3 weeks | Schneider, ABB, Siemens, LS Electric |
| VFD / drives | Variable speed drives | 4–16 weeks | ABB, Danfoss, Siemens, Rockwell, Yaskawa |
| PLC hardware | CPU, I/O modules, racks, comms | 4–12 weeks | Siemens, Allen Bradley, Schneider, Mitsubishi |
| Terminal blocks | Modular terminals, disconnect, IS terminals | 1–3 weeks | Phoenix Contact, Weidmuller, Wago, ABB |
| Instrumentation | Meters, transducers, IS barriers, relays | 2–6 weeks | Datexel, Yokogawa, Endress+Hauser, PR Electronics |
| Cable & wiring | Control cable, power cable, screened cable | 1–2 weeks | Prysmian, Nexans, Olex, Belden |

## 6.2 Procurement Risk & Lead Time Management

- Long-lead items (VFDs, PLCs, ACBs) should be identified at enquiry stage and ordered early

- Always confirm lead times with vendors at time of quotation – do not use historical data blindly

- Global supply chain events (e.g., chip shortages) can extend lead times significantly

- Specify acceptable alternatives in the BOM where the client permits substitution

- Confirm minimum order quantities (MOQs) for cable, terminals, and consumables

- Budget for expedite fees if project schedule requires faster delivery

⚠ Lead Time Warning VFDs and PLCs from major brands (Siemens, Allen Bradley, ABB) can have lead times of 16–26 weeks during high-demand periods. Always check current lead times at quotation stage and flag this in your estimate. Failure to order on time is one of the most common causes of panel project delays.

# 7. Technical Specifications & Compliance

## 7.1 Understanding Technical Specifications

Most projects include a technical specification document that defines the design, construction, testing, and documentation requirements for panels. The estimator must read the specification carefully and identify all requirements that affect cost.

## 7.2 Specification Compliance Matrix

A compliance matrix documents how each specification clause is met. It is submitted with the quotation to demonstrate technical compliance. Structure:

| Column | Content |
| --- | --- |
| Spec Clause No. | Reference number from the specification document |
| Requirement Summary | Brief description of what is required |
| Compliance Status | COMPLIED / COMPLIED WITH DEVIATION / NOT COMPLIED / NOT APPLICABLE |
| Proposed Solution | How the requirement is met (our design, product, standard) |
| Deviation Details | If deviation: explain what is proposed and why it is technically equivalent or superior |
| Document/Drawing Ref | Reference to supporting drawing, data sheet, or standard |

## 7.3 Common Specification Requirements & Cost Impact

| Specification Requirement | Cost Impact | Notes |
| --- | --- | --- |
| IEC 61439 type tested assembly | +5–15% | Requires verified assembly with test reports |
| IP65 or higher rating | +15–30% | Sealed enclosure, special cable glands, door seals |
| Stainless steel 316L enclosure | +200–400% | Over standard mild steel painted panel |
| ATEX/IECEx Zone 1 certification | +500–1000% | Specialist manufacturer, certified components only |
| SIL 2 PLC system | +100–200% | Redundant hardware, certified software, proof test |
| FAT with client witness | +5–10% | Preparation, support staff, travel if client is remote |
| As-built drawings (AutoCAD/EPLAN) | +3–8% | Depends on panel complexity and drawing suite size |
| Third-party inspection (DNV, Bureau Veritas) | +3–6% | Inspection fees, hold point management |
| Redundant CPU and PSU | +30–60% | Duplicated hardware, additional commissioning |
| 5-year parts warranty | +3–8% | Extended warranty provision |

# 8. Factory Acceptance Testing (FAT)

## 8.1 What is a FAT?

A Factory Acceptance Test (FAT) is a witnessed test performed at the panel manufacturer's workshop before the panel is shipped to site. The client (or their representative) witnesses the tests to verify the panel meets the specification.

## 8.2 Typical FAT Scope for Each Panel Type

### MCC FAT Checklist

- Visual inspection: Compare against approved drawings, check nameplates, labels, wiring neatness

- Insulation resistance test: Each circuit to earth (minimum 1 MΩ at 500VDC / 1000VDC)

- High voltage dielectric test (HV test): Verify insulation withstand (typically 2kV for 1 minute)

- Continuity test: All control and power circuits verified against schematics

- Functional test: Operate each motor starter – start, stop, overload trip simulation

- Protection relay test: Test overload trip, earth fault trip, under-voltage release

- Interlock verification: Confirm all electrical and mechanical interlocks operate correctly

- Metering check: Verify current and power metering accuracy

- Bus bar torque check: Verify all busbar bolts torqued to manufacturer's specification

### VFD FAT Checklist

- Visual inspection and drawing check

- Insulation resistance test (de-energise drive before testing – capacitor discharge required)

- Power-up sequence test: Verify control power, drive fault-free status

- Parameter setting verification: Check all programmed parameters against data sheet

- Run test (with load bank or motor simulator): Verify speed control, ramp, acceleration

- Bypass circuit test (if fitted): Verify changeover without drive fault

- Fieldbus communication test: Verify drive appears on network with correct address

- Protection test: Simulate overcurrent, under-voltage, overtemperature trips

### PLC FAT Checklist

- Hardware configuration check: Verify all modules installed per approved I/O schedule

- Power-on test: Verify CPU runs without faults, all I/O modules healthy

- I/O forcing test: Force each DI/DO/AI/AO channel and verify physical response

- Analogue loop accuracy: 0%, 25%, 50%, 75%, 100% signal injection, verify reading

- Communication test: Verify all fieldbus and network connections active

- UPS test: Disconnect mains, verify UPS maintains power for specified holdover time

- Functional (logic) test: Simulate process conditions, verify PLC sequence logic

- SCADA connectivity test: Verify all tags visible and updating in SCADA/DCS

## 8.3 Costing a FAT

| FAT Cost Element | Calculation Method | Typical Cost |
| --- | --- | --- |
| Test preparation (internal) | Hours × labour rate | 16–40 hrs per panel |
| Test equipment (loop calibrator, megger, HV tester) | Allow as fixed cost or amortise over projects | $500–1500 per test |
| Technical staff during FAT | Days × rate (supervision) | 1–3 days per panel |
| Documentation preparation | Hours × rate | 8–16 hrs (test reports, punchlist) |
| Punchlist rectification allowance | Risk allowance – 5% of FAT cost | Typically $500–2000 |
| Load bank hire (VFD functional test) | Day hire rate | $300–800/day |
| Client travel/accommodation (if remote) | Pass-through cost – clarify with client | Variable |

# 9. Quotation Development & Presentation

## 9.1 Quotation Document Structure

- Cover page: Project name, client, revision, date, contact details

- Executive summary: Scope overview, key assumptions, delivery schedule

- Scope of supply: Detailed description of what is included and excluded

- Technical specification compliance matrix: Clause-by-clause response

- Bill of Materials summary: Itemised material cost by section

- Labour schedule: Hours by activity and labour category

- Delivery schedule: Manufacturing timeline from order to delivery

- Commercial terms: Payment terms, warranty, validity period, escalation clause

- Exceptions and clarifications: List of all assumptions and deviations

## 9.2 Inclusions & Exclusions – Common Examples

| Item | Typically INCLUDED | Typically EXCLUDED |
| --- | --- | --- |
| Panel manufacturing | Yes – factory build | Site installation labour |
| Factory testing (routine) | Yes – standard | Witnessed FAT (may be optional) |
| As-built drawings | Negotiated – clarify | Software programming (PLC/HMI) |
| Spare parts | Not included unless specified | Commissioning support |
| Freight to site | Ex-works typical; DDP if specified | Site civil/structural work |
| Cable glands | Supply only – panel side | Field cable supply and installation |
| Consumables (cable ties, ferrules) | Yes – included in BOM | Gloves, PPE, site safety gear |
| Documentation | GA drawings, schematic, BOM | HAZOP study, risk assessment |

## 9.3 Pricing Strategy & Margin Application

| Cost Element | Description | Typical % |
| --- | --- | --- |
| Direct material cost | BOM at buy price (ex-GST) | Base |
| Material mark-up / handling | Administration, procurement overhead | +5–10% |
| Direct labour cost | Hours × award rate | Base |
| Labour overhead | Supervision, tooling, workshop overhead | +40–60% on labour |
| Sub-contractor cost | If any sub-contracted work | Base |
| Project overheads | Engineering, drawing, PM, QA | +8–15% on total cost |
| Risk / contingency | Depends on scope definition clarity | +3–10% |
| Profit margin | Company margin target | +10–20% |
| Escalation (if long project) | Material price increase allowance | +2–5% per year |

# 10. Week 2 Assessment Guide

## 10.1 Design & Layout Questions

- What enclosure material would you specify for a panel installed in a coastal fish processing facility?

- A VFD panel contains three 45kW VFDs. Estimate the total heat dissipation and recommend a cooling solution.

- What clearances must be maintained in an MCC panel between horizontal cable duct rows?

## 10.2 BOM & Estimation Questions

- List the key sections of a PLC panel BOM and name two items in each section.

- A project requires 140 DI, 80 DO, 35 AI, and 20 AO with 25% spare. Using 16-channel modules, how many of each module type are required?

- What consumables are commonly omitted from panel BOMs and what is the approximate cost impact?

## 10.3 Labour Estimation Questions

- Estimate the total labour hours for an MCC with 12 DOL starters and 4 star-delta starters (excluding enclosure preparation and bus work).

- What multiplier would you apply to labour for a panel requiring ATEX Zone 1 certification?

- How many labour hours would you estimate for a PLC panel with 300 marshalled I/O points?

## 10.4 FAT & Commercial Questions

- Name five tests included in a standard MCC FAT.

- A client requests a witnessed FAT for three VFD panels. They are based interstate. List the cost elements you would include in the FAT quote.

- What is the typical validity period for a panel quotation and why does it have a time limit?

# 11. Week 2 Additional Glossary

| Term | Definition |
| --- | --- |
| BOM | Bill of Materials – complete itemised list of all components, quantities, and costs |
| CT (current transformer) | Instrument transformer used to step down current for metering and protection |
| Derating | Reducing a component's rated capacity due to operating conditions (temperature, grouping) |
| dV/dt filter | Output filter on VFD that reduces rate of voltage rise to protect motor insulation |
| DXA | Twips unit (1/1440 inch) used in Word document formatting |
| EPLAN | Electrical engineering CAD software commonly used for panel schematic design |
| Ex-works (EXW) | Incoterms delivery condition where buyer collects from seller's factory |
| FAT | Factory Acceptance Test – witnessed testing at manufacturer's workshop |
| Form of separation | IEC 61439 classification defining degree of internal separation in assemblies |
| GRP | Glass Reinforced Polyester – fibreglass enclosure material |
| Heat exchanger (panel) | Air-to-air device maintaining sealed IP rating while removing panel heat |
| Incoterms | International commercial terms defining delivery and risk transfer point |
| IS barrier | Intrinsic safety barrier – limits energy in hazardous area circuits |
| LSZH | Low Smoke Zero Halogen – cable jacketing material, reduced toxic fumes in fire |
| MOQ | Minimum Order Quantity – minimum purchase quantity from a vendor |
| Punch list | List of deficiencies identified during FAT that must be rectified |
| SAT | Site Acceptance Test – testing performed after installation at site |
| THD | Total Harmonic Distortion – measure of waveform distortion from fundamental frequency |
| VT (voltage transformer) | Instrument transformer used to step down voltage for metering |

End of Week 2 Study Document

Prepared for GET Estimation & Costing Engineer Training Program  |  Panel Design, Specifications & Detailed Estimation